## Sheet1
vuln_string | med_Slight | med_Moderate | med_Extensive | med_Complete | beta_Slight | beta_Moderate | beta_Extensive | beta_Complete | description
ESS1 | 0.15 | 0.29 | 0.45 | 0.9 | 0.7 | 0.55 | 0.45 | 0.45 | Low Voltage (115 KV) Substation (Anchored/Seismic Components)
ESS2 | 0.13 | 0.26 | 0.34 | 0.74 | 0.65 | 0.5 | 0.4 | 0.4 | Low Voltage (115 KV) Substation (Unanchored/Standard Components)
ESS3 | 0.15 | 0.25 | 0.35 | 0.7 | 0.6 | 0.5 | 0.4 | 0.4 | Medium Voltage (230 KV) Substation (Anchored/Seismic Components)
ESS4 | 0.1 | 0.2 | 0.3 | 0.5 | 0.6 | 0.5 | 0.4 | 0.4 | Medium Voltage (230 KV) Substation (Unanchored/Standard Components)
ESS5 | 0.11 | 0.15 | 0.2 | 0.47 | 0.5 | 0.45 | 0.35 | 0.5 | High Voltage (500 KV) Substation (Anchored/Seismic Components)
ESS6 | 0.09 | 0.13 | 0.17 | 0.38 | 0.5 | 0.4 | 0.35 | 0.35 | High Voltage (500 KV) Substation (Unanchored/Standard Components)
EPP1 | 0.1 | 0.21 | 0.48 | 0.78 | 0.55 | 0.55 | 0.5 | 0.5 | Small Generation Facility (Anchored Components)
EPP2 | 0.1 | 0.17 | 0.42 | 0.58 | 0.5 | 0.5 | 0.5 | 0.55 | Small Generation Facility (Unanchored Components)
EPP3 | 0.1 | 0.25 | 0.52 | 0.92 | 0.6 | 0.6 | 0.55 | 0.55 | Medium/Large Generation Facility (Anchored Components)
EPP4 | 0.1 | 0.22 | 0.49 | 0.79 | 0.6 | 0.55 | 0.5 | 0.5 | Medium/Large Generation Facility (Unanchored Components)
EDC1 | 0.28 | 0.4 | 0.72 | 1.1 | 0.3 | 0.2 | 0.15 | 0.15 | Distribution Circuit (Seismic Components)
EDC2 | 0.24 | 0.33 | 0.58 | 0.89 | 0.25 | 0.2 | 0.15 | 0.15 | Distribution Circuit (Standard Components)
TLAS | 0.75 | 0.75 | 0.75 | 0.75 | 0.7 | 0.7 | 0.7 | 0.7 | Low voltage transformer with anchored subcomponents
TLUS | 0.5 | 0.5 | 0.5 | 0.5 | 0.7 | 0.7 | 0.7 | 0.7 | Low voltage transformer with unanchored subcomponents
TMAS | 0.6 | 0.6 | 0.6 | 0.6 | 0.7 | 0.7 | 0.7 | 0.7 | Medium voltage transformer with anchored subcomponents
TMUS | 0.3 | 0.3 | 0.3 | 0.3 | 0.7 | 0.7 | 0.7 | 0.7 | Medium voltage transformer with unanchored subcomponents
THAS | 0.4 | 0.4 | 0.4 | 0.4 | 0.7 | 0.7 | 0.7 | 0.7 | High voltage transformer with anchored subcomponents
THUS | 0.25 | 0.25 | 0.25 | 0.25 | 0.7 | 0.7 | 0.7 | 0.7 | High voltage transformer with unanchored subcomponents